APPENDIX "B"

Our Ref.:

Your Ref.:

District Official

Nicosia District Town Planning Office

109 Prodromos Avenue Strovolos

Town Planning & Housing Department

1454 Nicosia

Date

Dear Sir,

Application for the Issue of Permit …………………………..

Area …………………..  Plot ………………………….  Sheet/Plan ………………………..

The EAC’s views on the above matter are as follows:

Under Conditions due to Transmission Line

The applicant’s plot is traversed by transmission line 132KV in the vicinity of the proposed development.

With this opportunity I wish to draw your attention to the provisions of clause 32(i) of the Electricity Law CAP170 on the basis of which building under or near an overhead electric line is not allowed unless the EAC’s written consent has been secured.

As you know following a serious study of the problems and worries by the public about the existence of overhead electric lines near inhabited areas, it has been deemed necessary in the case of erection of buildings near transmission lines 132KV to leave a "strip of Land" of 25m width under the line (i.e. 12.50m on either side of the axis of the line).

The exact route of the EAC’s line should be surveyed and verified on site on behalf of the applicants.

The EAC would not therefore raise an objection provided:

- No part of the building will lie at a horizontal distance of less than 15.50m from the axis of the line

- If there will be any change in the ground level under the line such change would not reduce today’s clearances of the conductors of the Line from the ground.  If there will be a reduction in the clearance, the matter should be referred to the EAC for further study.

Finally, you are requested to draw the attention of the owners and of their contractors of the development to the existence of the overhead electric line and the dangers which this fact entails in order to avoid any possible accidents.

Underground Distribution Network affected

In areas where work will be carried out in connection with the proposed development there is underground network which will e affected.

With this opportunity I would like to draw your attention to the provisions of clause 32(i) of the Electricity Law CAP170 on the basis of which building near the electrical network of the EAC is not allowed unless the EAC’s written consent has been secured.

The EAC does not object to the issue of the Permit applied for, subject to the following terms:

- The applicant will apply to the Drawing Office of our Area before commencement of any work so that the exact position of the underground cables be indicated to him on site

- If it transpires that the underground electric network is affected and should be resited,  the applicant should apply in time to our Office and at any rate before starting any construction work for the resiting  of the underground cables.

Finally, I would request you to draw the attention of the owners and the contractors of the development to the existence of the underground cables and to the dangers which this fact entails, in order to avoid any possible accidents.

Substation Agree

In connection with the above building which consists of:

XX	Floors

Parking at Basement/Ground Level

XX	Flats

XX	Offices

XX	Shops

XX	Stores

XX	Workshops

i  wish to inform you that the Electricity Authority does not raise an objection to the issue of the Permit applied for subject to the following terms:

For adequate supply of electricity to the proposed development it is necessary to establish a ground-mounted substation in the area of the building and lay an underground cable service.

In view of the above I would request that among the other terms you would like to impose on the applicant, you include the above terms of the Electricity Authority. For the electrical Substation there will be a need to issue a separate title deed which will also cover the night of access to the substation as well as the right of laying and maintaining underground cables.

The position and the dimensions of the electrical substation have been agreed between competent officers of our Office and the architect of the applicants, as indicated on the attached architectural plans which beat the signature and stamp of the responsible Officer.

Construction of the substation should be carried out on the basis of the architectural plans agreed and in line with the requirements and specifications of the EAC. Supervision of construction is the responsibility of the applicant and should be carried out by the Supervising Engineer of the development.

The Substation will be taken over only when it is ascertained by competent Officers of the EAC that it has been constructed in accordance with above mentioned requirements of the EAC.

Failure to satisfy the requirements of the EAC may result in increased costs as well as delays in the electrification of the development.

For the timely electrification of the development the applicants should submit their application to the EAC as soon as construction works commence.

Comment

In the event that there are no changes in the plans of the applicants it will not be necessary to forward the Application Folder for the EAC’s views,   but you are requested to include the above terms in the relevant terms for the issue of the Permit applied for.

In the event that changes be affected to the plans of the applicants, which affect the decision of the Electricity Authority regarding the position, dimensions and access to the Substation such as, increase in the magnitude of the building, modification of the communal spaces etc, it will be necessary to forward the Application Folder to EAC, for the revised views of the Electricity Authority.

Thanking you for your cooperation

Yours faithfully

Costas Kokkinos

Assistant Area Manager

(System Planning)

Competent Officer for Communication: __________________ Tel. _________ Fax._________

___________________Tel. _________ Fax._________

Incl. ______________

CC. ______________